## Sheet1
| Quality Channel A | Quality Channel B | Quality Channel C | Configuration | Voting Result
DI | Normal | Normal | Normal |  | Result of 2oo3
| Normal | Normal | Bad | 2oo2 | Result of 2oo2
|  |  |  | 1002 | Result of 1oo2
| Normal | Bad | Bad |  | Channel A's value
| Bad | Bad | Bad |  | Value set by user
DO | Normal | Normal | Normal |  | Result of 2oo3
| Normal | Normal | Bad | 2oo2 | Result of 2oo2
|  |  |  | 1002 | Result of 1oo2
| Normal | Bad | Bad |  | Channel A's value
| Bad | Bad | Bad |  | Safety value
AI | Normal | Normal | Normal |  | Median
| Normal | Normal | Bad |  | Mean
| Normal | Bad | Bad |  | Channel A's value
| Bad | Bad | Bad |  | Value set by user
AO | Normal | Normal | Normal |  | Median
| Normal | Normal | Bad |  | Mean
| Normal | Bad | Bad |  | Channel A's value
| Bad | Bad | Bad |  | Safety value
The validity of input channel relies on its quality which includes the quality of data, the quality of IP_BUS and the quality of PM_BUS. If the quality is bad, the channel will be isolated in voting. The validity of output channel relies on its quality which includes the quality of data and the quality of PM_BUS. If the quality is bad, the channel will be isolated in voting. If an analog data is out of the tolerance, the quality is bad and the channel will be isolated in voting.