## Slide 1: Gamma System Safety Concept
Aug, 11th, 2015

## Slide 2: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 3: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 4: System overview
Scope: logic solver
Type: PES
Figure (integrated in system)

## Slide 5: System overview

## Slide 6: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 7: Safety requirements
Application (Both safety and control)
  ESD, ETS, BMS, FGS
  ITCC, HIPPS
  Process control
Certification
  FS&S: SIL3, SC3, SL1(2?)
  ISASecure: EDSA-311 & 312, SDLA(?), SSA(?)
  CE: EMC, LVD, ATEX(?)
  FM(?)
  ISO 9000 (Company level)

## Slide 8: Safety requirements
Codes and standards
  IEC 61508 Parts 1-7:2010
  IEC 61511 Parts 1-3:2004(2015?)
  IEC 61131-2:2007
  IEC 61131-6:2012
  EN 50156-1:2004
  EN 298:2012
  EN 13611:2007+A2:2011
  NFPA 85:2015
  NFPA 86:2015

## Slide 9: Safety requirements
Codes and standards (continued)
  EN 54-2:1997+AC:1999+A1:2006
  NFPA 72:2013
  EN 50130-4:2011
  EN 50178:1997
  IEC 61000-6-2:2005
  IEC 61000-6-4:2006
  IEC 61326-1:2012
  IEC 61326-3-1:2008
  IEC 61010-1:2010
  IEC 61010-2-201:2013

## Slide 10: Safety requirements
Codes and standards (continued)
  IEC/NP 62443-4-1:2013
  IEC/NP 62443-4-2:2013
  ISASecure EDSA-311:2010
  ISASecure EDSA-312:2015
  ISASecure SDLA (?)
  ISASecure SSA (?)
  ANSI/ISA 84.00.01-1:2004
  IEC 62061:2012 (OSP module only)

## Slide 11: Safety requirements
System scale (maximum)
  64 control stations and 16 PCs (Engineer/ operator/ diagnostic/ SOE station…)
  1x MC (main chassis) + 14x EC (extension chassis)
  3680 digital points/ 1248 analog points

## Slide 12: Safety requirements
I/O type
  Analog input: SIL3, 32 inputs, 4~20mA, 2-/ 3-/ 4-wire, HART, SOE
  Digital input: SIL3, 32 inputs, 24VDC, Type 3, SOE
  Analog output: SIL3, 16 outputs, 4~20mA, HART
  Digital output: SIL3, 32 outputs, 24VDC, DC-13
  Over-speed protection: SIL3, standalone loop, 6x PI/ 4x DI/ 4x DO
  Specific process control modules: non-safety related

## Slide 13: Safety requirements
System response time
  30ms DI DO @ 300 points, typical configuration
OSP module response time
    12ms PI DO
Mode of operation (including OSP)
    Low demand
    High demand
    Continuous

## Slide 14: Safety requirements
PFDav/ PFH (including OSP)
  Less than 10% of SIL3
PTI (including OSP)
  More than 10 years
Safe state (including OSP)
  Digital output: ‘0’
  Analog output: 0mA
SIL3 @ 2x PMs
System start-up @ 1x PM

## Slide 15: Safety requirements
Power supply
  AC/DC: 100VAC~ 240VAC (-15%~ +10%) @ 47~ 63Hz, SELV/ PELV
  DC/DC: 24VDC (18VDC~ 31.2VDC)
  Dual redundant
  Diagnostic measures of power supply can identify the faulty power supply module

## Slide 16: Safety requirements
Safety communication
  IP Bus: between PM & I/O modules
  PM Bus: between PMs
  Peer to peer: between control stations
  All proprietary

## Slide 17: Safety requirements
Working environment
  Operating temperature: -10～60°C
  Storage temperature: -40～85°C
  Humidity: 5%~ 95%, non-condensing
  Type of protection: IP20 (modules in chassis)
  Protection class: Class II acc. IEC 61131-2
  Pollution: Pollution degree II acc. IEC 61131-2
  Altitude: < 3000m

## Slide 18: Safety requirements
Non-safety requirements
  Standard 19-inch cabinet mounting
  Redundancy for availability supported at I/O modules and communication
  Timing & SOE
  Temperature monitoring at each PM, CM & I/O modules

## Slide 19: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 20: Safety concept – Overview
Data flow
  System

## Slide 21: Safety concept – Overview
Data flow
  OSP module

## Slide 22: Safety concept – Overview
Reliability block diagram – system
  TMR part: Type B, HFT=1, SFF≥90%
  1oo1 part: Type A, HFT=0, SFF≥90%
  System & field power supplies: Type B, HFT=0, SFF≥99%, redundant for availability

## Slide 23: Safety concept – Overview
Reliability block diagram – OSP module
  TMR part: Type B, HFT=1, SFF≥90%
  1oo1 part: Type A, HFT=0, SFF≥90%
  System & field power supplies: Type B, HFT=0, SFF≥99%, redundant for availability

## Slide 24: Safety concept – Overview
Control/ Safety property
  User configurable parameters in configuration software
  Detailed description in safety manual
Affected aspect | Safety | Control
Voting scheme (PM) in Dual mode | 1oo2 (3-2-0), fixed | 1oo2 (3-2-0) or 2oo2 (3-2-1-0), configurable
Output state of DO & AO modules when IP Bus has fault | Safe state | Safe state or keep the latest valid value, configurable

## Slide 25: Safety concept – Overview
Degradation modes – system
  3x PMs: 3-2-1-0 (control), 3-2-0 (safety)
  2x PMs: 2-1-0 (control), 2-0 (safety)
Degradation modes – OSP module
  3-2-0

## Slide 26: Safety concept – Overview
Fault detection and management
  Periodical (≤24h) & power-on diagnostics
  Faults in modules functionality, power supply, field connection, communication, temperature, etc.
  Alarms both on module indicators & PCSW interface
Action after detection of failure
  Safety related: comply to IEC 61508
  Non-safety related: only alarm

## Slide 27: Safety concept – Overview
Noise filtering (Safety function & fault detection)
  User configurable parameters in configuration software
  Detailed description in safety manual
Safety function | Without noise filtering | With noise filtering
Output voting in PM | No output delay after voting | Output delay n cycles
Output voting in DO & AO modules | No output delay after voting | Output delay n cycles
Fault detection | Without noise filtering | With noise filtering
IP Bus faults | No delay after voting | Alarm & action delay n cycles
Module faults | No delay after voting | Alarm & action delay n cycles
Field connection faults | No delay after voting | Alarm & action delay n cycles

## Slide 28: Safety concept – Overview
System response time (calculation & allocation)

## Slide 29: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 30: Safety concept – HW subsystem
Hardware subsystem block diagram

## Slide 31: Safety concept – HW subsystem
Power supplies & grounding scheme
  System-side power supplies located in each MC & EC
  Power supplies for field instruments located in cabinets & output via ETP

## Slide 32: Safety concept – HW subsystem
Processor module (PM) block diagram
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 33: Safety concept – HW subsystem
Analog input module (AI) block diagram (including ETP)
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 34: Safety concept – HW subsystem
Digital input module (DI) block diagram (including ETP)
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 35: Safety concept – HW subsystem
Analog output module (AO) block diagram (including ETP)
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 36: Safety concept – HW subsystem
Digital output module (DO) block diagram (including ETP)
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 37: Safety concept – HW subsystem
Over-speed protection module (OSP) block diagram (including ETP)
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 38: Safety concept – HW subsystem
Power supply module (PW) block diagram
RBD
Power supply
Diagnostic measures for random HW failures
Action after detection of failure

## Slide 39: Safety concept – HW subsystem
Bus interface module (BI) block diagram
Safety function & diagnostic measures (detailed in MC part)

## Slide 40: Safety concept – HW subsystem
Main chassis (MC) & extension chassis (EC)
  Module addressing (including BI module)
  Key-switch on MC (non-safety related)

## Slide 41: Safety concept – HW subsystem
Non-safety related modules
  Communication module (CM) block diagram
  Specific process control modules
Impact analysis of non-safety related modules

## Slide 42: Safety concept – HW subsystem
Safety related parameters calculation
  Referenced standard: Telcordia SR-332, 2011, issue 3

## Slide 43: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 44: Safety concept – ESW subsystem
Embedded software subsystem scope
  PM ESW
  IO module ESW
  BI ESW
  CM ESW
Safety related issues
  Programming languages subset with coding standards
  Cyclic behavior with guaranteed maximum cycle time
  Multi-tasking design
  Static analysis & dynamic analysis/ testing

## Slide 45: Safety concept – ESW subsystem
PM ESW
  CPU SW functionality block diagram
  Download
  Download change
  Arithmetic execution
  Algorithm library design
  Write variable
  Data monitoring
  System states
  Multi-tasking design
  FPGA & CPLD FW block diagram

## Slide 46: Safety concept – ESW subsystem
IO module ESW
  MCU FW block diagram
  MCU FW states
  FPGA & CPLD FW block diagram

## Slide 47: Safety concept – ESW subsystem
BI module ESW
  FPGA & CPLD FW block diagram

## Slide 48: Safety concept – ESW subsystem
CM module ESW
  CPU SW block diagram
  CPU SW states
  OS
  FPGA & CPLD FW block diagram

## Slide 49: Safety concept – ESW subsystem
PM Bus safety communication
  OSI model
  Frame structure
  Safety measures
  Action after detection of failures
  Calculation

## Slide 50: Safety concept – ESW subsystem
IP Bus safety communication
  OSI model
  Frame structure
  Safety measures
  Action after detection of failures
  Calculation

## Slide 51: Safety concept – ESW subsystem
Peer-to-peer safety communication
  OSI model
  Frame structure
  Safety measures
  Action after detection of failures
  Calculation

## Slide 52: Safety concept – ESW subsystem
Offline SW tools
  T3
  T2
  T1

## Slide 53: Safety concept – ESW subsystem
FPGA/ CPLD related measures for avoidance of systematic failures

## Slide 54: Safety concept – ESW subsystem
COTS components
Reused components

## Slide 55: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 56: Safety concept – PSW subsystem
PC software subsystem scope
  Configuration SW
  Diagnostic SW
  SOE SW
  OPC server
  AMS SW
Safety related issues
  Validity after compiling
  Protection of disk files
  Data integrity during download
  IAC & UC

## Slide 57: Safety concept – PSW subsystem
Configuration software
  Supported programming languages
  Functionality diagram
  Block diagram
  Operation modes
  Validity after compiling
  Protection of disk files
  Data integrity during download
  IAC & UC

## Slide 58: Safety concept – PSW subsystem
Diagnostic software
  Functionality diagram
  Block diagram
  Operation modes
  Protection of disk files
  IAC & UC

## Slide 59: Safety concept – PSW subsystem
SOE software
  Functionality diagram
  Block diagram
  Operation modes
  Protection of disk files
  IAC & UC

## Slide 60: Safety concept – PSW subsystem
OPC server
  Functionality diagram
  Block diagram
  Operation modes
  Protection of disk files
  IAC & UC

## Slide 61: Safety concept – PSW subsystem
AMS software
  Functionality diagram
  Block diagram
  Operation modes
  Protection of disk files
  IAC & UC

## Slide 62: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 63: Safety concept – Type testing
Test items
  EMC tests
  Mechanical tests
  Climatic tests
  Electrical tests
Detailed in SRS

## Slide 64: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 65: Safety concept – Security
Product development lifecycle (IEC 62443-4-1)
  SMP
  SecRS
  SAD
  SRA
  DD
  DSG
  MIV
  SIT
  SPV
  SDM
  SVT
  SRE

## Slide 66: Safety concept – Security
SMP (Security management process)
  Overall planning described in Safety Plan (including security)
  Identification of responsibilities
  Identification of applicability (lifecycle tailoring regarding project)
  Security expertise/ Periodical training
  Action item resolution (documented and tracked)
  Configuration management (as required by IEC 61508)
  Bug management (including unfixed security bug list)

## Slide 67: Safety concept – Security
SecRS (Security requirement specification)
  Overall described in SRS (including security)
  Product description (type/ scope/ boundary, physical/ logical)
  Security requirements (installation, operation, maintenance, decommissioning)
  Expected security environment
  Security functions/ features
  Complied regulations
  IEC 62443-3-3 requirements
  Review of SecRS (Participants: development, test, marketing)

## Slide 68: Safety concept – Security
SAD (Security architecture design)
  Overall described in SSC, HWSC, ESWSC & PCSW-OD (including security)
  Addresses requirements in SecRS (including functions and data)
  System partition (into subsystems/ components/ layers/ domains)
  Interface design
  Identification of data resources
  Enumerate the attack surfaces (including all possible entry points)
  Reduction of attack surfaces to those absolutely necessary
  Security design best practice

## Slide 69: Safety concept – Security
SRA (Security risk assessment and threat modeling)
  Separate document
  Risk assessment to determine which component affects security and to plan which component requires threat modeling (How?)
  Threat modeling to identify vulnerabilities in security architecture (What? How?)
  Vulnerabilities prioritization after threat modeling(How?)
  Vulnerabilities mitigation for those above the defined security level

## Slide 70: Safety concept – Security
DD (Detailed design)
  Detailed described in module design documents
  Security design best practice (creating checklist for reviewing)
  Input validation of data crossing trust boundary
  Design review

## Slide 71: Safety concept – Security
DSG (Document security guidelines)
  Separate document
  User document security guidelines for administrators and users
  Maintenance instructions
  User manual review
  Security tools to assist in configuration and audit of the product
  Legacy code which is not fully compliant with this standard (if any)

## Slide 72: Safety concept – Security
MIV (Module implementation & verification)
  Detailed described in module testing documents
  Secure coding guideline as part of overall coding guideline (tbd)
  Code review, especially code with high privilege
  Automated static security analysis & mitigation of violation
  Unit testing at branch level
  Security of COTS OS
  Secure installation by default
  Static binary analysis & risk mitigation of third-party components (tbd)
  Vulnerability monitoring of third-party components

## Slide 73: Safety concept – Security
SIT (Security integration testing)
  Detailed described in system integration testing documents
  Security integration testing plan
  Network robustness testing including DoS & fuzz tests for all protocols and interfaces (equipment?)
  Abuse case testing (What? How?)

## Slide 74: Safety concept – Security
SPV (Security process verification)
  Planned in SP & VVP, detailed described in V&V documents
  Both internal & external (TUV Rheinland) assessment

## Slide 75: Safety concept – Security
SDM (Security defect management)
  Planned in SP & VVP, detailed described in V&V documents
  Established procedure for vulnerability reporting and response
  Modification management
  Impact analysis for modification

## Slide 76: Safety concept – Security
SVT (Security validation testing)
  Planned in SP & VVP, detailed described in V&V documents
  Dynamic analysis/ testing (main) in conjunction with static analysis
  Validation planning & test case generation
  Documentation of validation results

## Slide 77: Safety concept – Security
SRE (Security response execution)
  Planned in SP & VVP, detailed described in company level QA documents
  Procedures for releasing fixes for significant security defects
  Procedures for notifying customers of significant security defects
  Procedures for timely validation of COTS security patches

## Slide 78: Safety concept – Security
Technical security requirements for components (IEC 62443-4-2)
  FR 1: IAC
  FR 2: UC
  FR 3: SI
  FR 4: DC
  FR 5: RDF
  FR 6: TRE
  FR 7: RA
  ACR: Application requirements
  ECR: Embedded device requirements

## Slide 79: Safety concept – Security
Overall constraints
  Control station  Embedded device, PCSW  Application
  Host device & Network device are out of range of the product
  Each CR in IEC 62443-4-2 are addressed
  Each SR in IEC 62443-3-3 are referenced

## Slide 80: Safety concept – Security
FR 1: IAC
CR | Implementation | Implemented RE | SL
1.1 IAC of human, process & device | Used. IAC for all human users | (1) Unique IAC of human users | SL1: CR 1.1 SL2: CR 1.1 (1), tbd
1.2 IAC of SW process & device | Used. Identify itself & authenticate with any other component | (1) Unique IAC itself to any other component | SL2: CR 1.2 SL4: CR 1.2 (1), tbd
1.3 Account management | Used. Account management capability provided |  | SL4: CR 1.3
1.4 Identifier management | Used. Management of identifiers supported |  | SL4: CR 1.4
1.5 Authenticator management | Used. Support use of initial authenticator content, recognition of changes to default authenticators, proper functioning with periodic change/refresh operation, and protection from unauthorized disclosure or modification | (1) Authenticators protected via HW mechanism | SL2: CR 1.5 SL4: CR 1.5 (1), tbd

## Slide 81: Safety concept – Security
FR 1: IAC (continued)
CR | Implementation | Implemented RE | SL
1.7 Strength of password-based authentication | Used. Support configurable password strength based on minimum length & variety of character types | (1) Password generation & lifetime restrictions for human users | SL2: CR 1.7 SL4: CR 1.7 (1), tbd
1.8 PKI certificates | Not used. Requirement of ND? |  | tbd
1.9 Strength of public key authentication | Not used. Requirement of ND? |  | tbd
1.14 Strength of symmetric key authentication | Not used. Requirement of ND? |  | tbd

## Slide 82: Safety concept – Security
FR 2: UC
CR | Implementation | Implemented RE | SL
2.1 Authorization enforcement | Used. Authorization for all human users | (1) Authorization for all users (2) A authorized role to define and modify the mapping of permissions to roles for all human users (3) Support supervisor manual override for a configurable time or sequence of events (4) Dual approval of critical action | SL2: CR 2.1 (1) (2) SL2: CR 2.1 (1) (2) (3) (4), tbd
2.2 Wireless use control | Not used. Requirement of ND? |  | tbd
2.3 Use control for portable and mobile device | tbd |  | tbd

## Slide 83: Safety concept – Security
FR 2: UC (continued)
CR | Implementation | Implemented RE | SL
2.4 Mobile code | Used. In the event of using mobile code, support the capability of preventing execution of mobile code, requiring proper authentication and authorization for origin of the code, restricting mobile code transfer, and monitoring the use of mobile code | (1) Verify integrity of mobile code before execution | SL4: CR 2.4 (1)
2.8 Auditable events | Used. Generate records which are relevant to security with timestamp, source, category, type, event ID & results, including: access control, request errors, control system events, backup & restore event, configuration changes & audit log events |  | SL4, CR 2.8

## Slide 84: Safety concept – Security
FR 2: UC (continued)
CR | Implementation | Implemented RE | SL
2.11 Timestamps | Used. All auditable events have timestamps | (1) Timestamp synchronized with system-wide time source (2) Detection of unauthorized alteration of time source & cause an audit event upon alteration | SL3: CR 2.11 (1) SL4: CR 2.11 (1) (2), tbd

## Slide 85: Safety concept – Security
FR 3: SI
CR | Implementation | Implemented RE | SL
3.1 Communication integrity | Used. Protection of transmitted information |  | SL2: CR 3.1
3.4 SW & information integrity | Used. Support integrity checks on SW, configuration as well as recording & reporting the checking results | (1) Automatic notification upon discovery of unauthorized change | SL4: CR 3.4 (1)
3.8 Session integrity | tbd | tbd | tbd

## Slide 86: Safety concept – Security
FR 4: DC
CR | Implementation | Implemented RE | SL
4.1 Information confidentiality | tbd |  | tbd
4.3 Use of cryptography | Used. Password protected using md5 algorithm | tbd | tbd

## Slide 87: Safety concept – Security
FR 5: RDF
CR | Implementation | Implemented RE | SL
5.1 Network segmentation | Used. Support a segmented network |  | SL4: CR 5.1
5.4 Application or device partitioning | Not appropriate at component level |  | Not relevant

## Slide 88: Safety concept – Security
FR 6: TRE
  Not required at component level

## Slide 89: Safety concept – Security
FR 7: RA
CR | Implementation | Implemented RE | SL
7.1 DoS protection | Used. Continuous operation in degraded mode during DoS event | (1) Mitigate the effects of information flooding types of DoS events | SL4: CR 7.1 (1)
7.3 Control system backup | Used. Support backup of system states, and does not affect normal operation | (1) Backup reliability can be verified (2) Automatic backup based on configurable frequency | SL4: CR 7.3 (1) (2)
7.4 Control system recovery & reconstitution | Used. Support to recover and reconstitute to a know secure state after failure |  | SL4: CR 7.4

## Slide 90: Safety concept – Security
ACR: Application requirements
ECR: Embedded device requirements
HCR & NCR: Not relevant
CR | Implementation | Implemented RE | SL
3.2 Malicious code protection | Used. Detailed description of malicious code protection mechanisms & special configuration requirements |  | SL4: ACR 3.2
CR | Implementation | Implemented RE | SL
3.2 Malicious code protection | tbd |  | tbd
3.9 Originality | tbd |  | tbd

## Slide 91: Contents
System overview
Safety requirements
Safety concept
  Overview
  Hardware subsystem
  Embedded software subsystem
  PC software subsystem
Type testing issues
Functional security issues
Project schedule

## Slide 92: Safety concept – Project schedule
Schedule

## Slide 93
谢 谢